JOURNAL OF ENGINEERING AND

APPLIED SCIENCES

Journal of Engineering and Applied Sciences 12 (2018), 103-116

Contingency Analysis of 330kv Nigeria Network Uwaechi P. C, Ezechukwu O. A, Yisa. M.S, Okolie D. A Department of Electrical Engineering,

Nnamdi Azikiwe University, Awka. peter4gr8@gmail.com

Abstract

This paper highlights the contingency analysis of Nigeria 330kV network to examine the risk of possible contingencies posed to the network under generators outage condition. The problems of the system in future are equipment malfunctions, under voltage at various buses, shortage of reactive power support, increased transmission losses and the tendency of system collapse. The design and simulation of the network was carried-out using power world simulator. The analysis was done using Newton- Raphson AC power flow method. Thereafter, three generators outage applied in the network was resolved using double circuit and reactive power compensation remedial actions. Consequently, a stable network that ensured adequate power delivery to the end users was achieved.

Keywords: Contingency Analysis, Power Flow, Transmission losses, Remedial actions, System collapse, Power world simulator

# 1. Introduction

Component outages in the distribution systems account for the absolute majority of the faults that result in an interruption of supply for the end consumers (Billinton and Allan, 1994). The consequences to modern society of a large interruption of supply (blackout) in the transmission system are considerable high. Important and vulnerable functions in the society, such as telecommunication, heating and water supply, normally function a few hours after an interruption of supply. Local backup generators can be available for some of the critical functions in the society, but this requires an organized distribution of fuel to the affected areas. The associated cost for the society of a large scale interruption is significant (Wacker and Billinton, 1989).

Since an outage event in the transmission system can propagate and paralyze the society in a widespread geographical area, the system has been constructed to meet the high needs of reliability. It is generally designed, operated and planned with the deterministic N- 1 criterion of contingency analysis, which is a rule according to which the system must be able to withstand the loss of any principal single component (ENTSOE, 2007). Clearly this criterion provides a security margin against unwanted conditions in the system.

As some propose for new sources of power in order to meet up the Nigeria energy demand, it is important to examine the security level of the existing grid in order to devise a more defensive approach of operation. Transmission Company of Nigeria (TCN), projected to have the capacity of delivering 12,500 MW in 2013, now has the capacity of delivering about 4800 MW of electricity. Nigeria has a generating capacity of 5,228 MW but with peak production of 4500 MW against a peak demand forecast of 10,200MW. This shows that if the generation sector is to run at full production, the transmission grid will not have the capacity to handle the produced power reliably (Nigeria Compass, 2013). This goes a long way to tell that the 330 KV transmission system is not running effectively as expected. Therefore to maintain and ensure a secure operation of this delicate system, the need for contingency analysis cannot be over emphasized.

# 2.0 Contingency analysis

Contingency Analysis (CA) in the simplest of term is the “what if” scenario analysis that determines the effect of electric components (elements) outage, provides information used to prioritize facilities and operating condition available to the electric power system.

Contingencies are defined as potentially harmful disturbances that occur during the steady state operation of a power system (Chary, 2011). Contingencies can lead to some abnormalities such as over voltage at some buses, over loading on the lines, which if are unchecked, can lead to total system collapse.

Power system engineers use contingency analysis to predict the effect of any component failure. Periodically, maintenance operations are carried-out on generating units or transmission lines. During this, a unit is taken offline for servicing. The effect of this forced outage on other parts of the system can be observed using contingency analysis.

Contingency analysis and risk assessment are very important task to assess the ability of the network to provide electric power of sufficient quality to customer. It is defined as potentially harmful for steady state operation of an electrical network that can result in possible loss of part of the network like buses, lines, transformer and power unit of any network area. These problems are concerns in the planning and operation of the power system. In the planning, contingency analysis is used to examine the performance of a power system and the need for new generation or transmission expansion due to load growth. In the operation, contingency analysis assists engineers to operate the power system at a secure operating point where equipment are loaded within their safe limits and power is delivered to customers with acceptable quality standards.

Severe fault can lead to wide spread of voltage drop, transformer tripping, line overload, system collapse or equipment malfunctions. To avoid these problems, contingency analysis must be studied with different contingency levels to determine the corrective action. Adding new var sources and transmission’s equipment will improve the voltage profile, avoid transmission’s equipment overloading and reduce transmission losses.

There are various methods of contingency analysis which include the following:

- AC Load flow method

- DC Load flow method

- Z-Matrix method

- Performance Index method

Of all the above listed methods, AC power flow calculation is considered to be deterministic method which is accurate compared to DC power flow method. In deterministic method, line outages are simulated by actual removal of lines. AC power flow method is accurate but computationally expensive and excessively demanding of computational time.

# 3.0 Formulation of power flow equations

The apparent power injected into any i named bus is given as

Sj = Pj + jQj	(1)

In terms of bus voltage and conjugate of bus current, the apparent power injected into bus j is given as

j

Sj = Vj I∗	(2)

where;

Pj is the real power component of the power in bus j

Qj is the reactive power component of the power in bus j

Vj is the voltage at bus j

Ij is the current at bus j while,

Ij * is the conjugate of current at bus j

Combining equations (1) and (2) produces

j

Pj + jQj = Vj I∗	(3)

Usually, of the four parameters (real power, reactive power, bus voltage magnitude and voltage phase angle) only two are specified to identify the bus which predefines the type of bus in use. The current, Ij injected in or out of a bus is not specified and is initially unknown, so its conjugate Ij * cannot be determined ab initio. This constraint limits the use of equation (3). Since Vj is often specified for some buses, its conjugate can be found. Hence equation (3) can be replaced with its mathematical equivalent as

j

Pj – jQj = V∗ Ij	(4)

The application of Kirchoff’s Current Law (KCL) to an interconnection of n buses, the expression for the current Ij injected into any j bus is given as

n

Ij = ∑ Yjk Vk

k

For j, k = 1,2,3,..,n

(5)

Where, Yjk is the admittance for the transmission line between buses j and k. The substitution of equation (5) into

(4) gives

n

j

Pj − jQj = V∗ ∑ Yjk Vk

(6)

k

Comparing terms;

Pi represents the real part while Qj represents the negative imaginary part of the RHS of equation (6). Mathematically this becomes,

n

j

Pj = real part of V∗ ∑ Yjk Vk

(7)

k

n

j

Qj = − imaginary part of V∗ ∑ Yjk Vk

(8)

k

With Yjk = Gjk + jBjk recall that in their polar forms Yjk, Vj * and Vk are given as

Yjk = |Yjk|ejθjk = |Yjk| < θjk	(9)

j

V∗ = |Vj|e–jδj = |Vj| <– δj	(10)

Vj = |Vk|ejδk = |Vj| < δk	(11)

where, θik and δi are the phase angle of the admittance and the bus voltage respectively.

Substituting for Yjk, Vj * and Vk in equation (6) gives

n

Pj − jQj = |Vj|e–jδj ∑|Yjk|ejθjk |Vk| ejδk

k

n

Pj − jQj = |Vj| ∑|Yjk||Vk| ej(θjk –δj +δk)

k

This implies that

n

Pj − jQj = |Vj| ∑|Yjk||Vk| ej(θjk –δj +δk)	(12)

k

For j, k = 1,2,3,…,n

But noting that |A|eix = |A|<x = |A|cosx + j|A|sinx

Then equation (12) becomes;

n

Pj = |Vj| ∑|Yjk||Vk| cos(θjk – δj + δk)

k

(13a)

n

𝑄𝑗 = − |V𝑗| ∑|Y𝑗𝑘 ||V𝑘| sin(θ𝑗𝑘 – δ𝑗 + δ𝑘)

k

For j, k = 1,2,3,…,n

Equations (13a) and (13b) are called the power flow equations (Gupta, 2008).

(13b)

In setting up the Newton-Raphson numerical method, the power-flow expressions of equations (13a) and (13b) are employed because these equations are more flexible and convenient to work with in developing and computing the elements of Jacobian matrix than the use of equation (12).

# Modelling of line flows and losses

Once the number of iteration is complete, the computation of line flows and losses is implemented. To accomplish this, a different program is developed with the aid of the model derived. Thus, figure 1 is a one- line diagram of a transmission line between two buses i and k which is used as a model to derive the line flow and losses.

Fig. 1: Transmission line model for calculating line losses

If bus j was to have a higher voltage potential, then applying Kirchhoff’s Current Law at bus j and defined in the positive direction of j → k gives the line current, Ijk, as

Ijk = Ij + Ijo = Yjk (Vj + Vk ) + Yjo Vj	(14)

Similarly, applying the same KCL at bus k for Ijk which is considered positive in the direction k→j, this line current is given as

Ikj = −Ik + Iko = Yjk (Vk − Vj ) + Yko Vk	(15)

The complex power Sjk from bus j to k which represents the Line flow and that from k to j, Skj, are given as

jk

Sjk = Vj I∗	(16)

kj

Skj = Vk I∗	(17)

The power loss SLjk in line j - k is the algebraic sum of the power flows determined from equation (16) and (17)

SLjk = Sjk + Skj	(18)

These equations are the mathematical model requirement for simulating load flow and line losses using Newton Rasphson iterative method as implemented with PowerWorld Simulator.

# Network visualization

The single line diagram for the base case of Nigeria forty one bus network is shown in fig. 2 as captured from power world simulator. Base case voltage and line parameters used for modelling Nigeria 41 bus network (fig. 2) is represented in the table 1.0 and table 2.0 respectively

Fig. 2: Single line diagram of the base case for forty one bus model of Nigeria grid system

# Base case data

Table 1.0: Voltage parameters for base case

| Bus Records |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Number | Name | Nom kV | PU Volt | Volt (kV) | Load MW | Load Mar | Gen MW | Gen Mvar | Switched Shunts Mvar |
| 1 | Kebbi | 330 | 0.97127 | 320.518 | 150 | 60 |  |  |  |
| 2 | Kanji | 330 | 1 | 330 |  |  | 570 | -99.33 |  |
| 3 | Jebba | 330 | 0.99905 | 329.685 | 350 | 195 |  |  |  |
| 4 | Shiroro | 330 | 1 | 330 | 250 | 160 | 600 | 174.04 |  |
| 5 | Oshogbo | 330 | 1.00399 | 331.317 | 201 | 137 |  |  | 0 |
| 6 | Jebba gs | 330 | 1 | 0 |  |  | 578.4 | 8.42 |  |
| 7 | Katampe | 330 | 0.95000 | 312.708 | 350 | 220 |  |  |  |
| 8 | Mando | 330 | 1.01019 | 333.362 | 200 | 125 |  |  | 0 |
| 9 | Kumbotso | 330 | 0.99799 | 329.337 | 350 | 220 |  |  | 239.04 |
| 10 | Jos | 330 | 1.03809 | 342.569 | 250 | 125 |  |  | 129.32 |
| 11 | Gombe | 330 | 1.01049 | 333.463 | 160 | 95 |  |  | 142.95 |
| 12 | Yola | 330 | 0.95097 | 313.819 | 160 | 90 |  |  |  |
| 13 | Olunrunsogo | 330 | 1 | 330 | 130 | 70 | 60 | 95.46 |  |
| 14 | Damaturu | 330 | 1.0074 | 332.441 | 130 | 70 |  |  |  |
| 15 | Maiduguri | 330 | 1.01822 | 336.014 | 200 | 150 |  |  | 186.62 |
| 16 | Omotosho | 330 | 0.9793 | 323.169 | 300 | 188 |  |  | 230.17 |
| 17 | Benin | 330 | 1.00222 | 330.734 | 157 | 80 |  |  | 0 |
| 18 | Ajaokuta | 330 | 1.00003 | 330.009 | 100 | 55 |  |  |  |
| 19 | Geregu | 330 | 1 | 330 |  |  | 414 | -53.73 |  |
| 20 | Sapelle | 330 | 1 | 330 |  |  | 400 | -108.45 |  |
| 21 | Onitcha | 330 | 0.99666 | 328.898 | 115 | 42 |  |  |  |
| 22 | Delta | 330 | 1 | 330 |  |  | 450 | -37.99 |  |
| 23 | Ikeja.w | 330 | 0.9876 | 325.906 | 429 | 248 |  |  | 468.17 |
| 24 | Akangba | 330 | 0.97814 | 322.788 | 470 | 306 |  |  | 0 |
| 25 | Papalanto | 330 | 1 | 330 |  |  | 304 | 9.6 |  |
| 26 | Aja | 330 | 0.99279 | 327.622 | 455 | 286 |  |  |  |
| 27 | Egbin | 330 | 1 | 330 |  |  | 388.24 | 343.5 |  |
| 28 | Aladja | 330 | 0.99702 | 329.016 | 82 | 45 |  |  |  |
| 29 | Afam | 330 | 1 | 330 |  |  | 450 | -53.21 |  |
| 30 | Alaoji | 330 | 1 | 330 | 360 | 218 | 300 | 285.79 |  |
| 31 | Okpai | 330 | 1 | 330 | 130 | 80 | 450 | 45.11 |  |

JEAS ISSN: 1119-8109

| 32 | New.h | 330 | 0.99204 | 327.373 | 113 | 56 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 33 | Ayede | 330 | 0.99723 | 329.086 | 139 | 61 |  |  |  |
| 34 | Mambiya | 330 | 1 | 330 |  |  | 130.88 | -194.3 |  |
| 35 | Guarara | 330 | 1 | 330 |  |  | 300 | -79.43 |  |
| 36 | Markurdi | 330 | 1.02588 | 338.54 | 180 | 65 |  |  |  |
| 37 | Omoku | 330 | 1 | 330 | 185 | 79 | 250 | 131.85 |  |
| 38 | Ikot e | 330 | 0.99526 | 328.435 | 139.81 | 50 |  |  |  |
| 39 | Calabar | 330 | 1 | 330 |  |  | 800 | -43.54 |  |
| 40 | Owerri | 330 | 0.99519 | 328.412 | 180 | 75 |  |  |  |
| 41 | Egbema | 330 | 1 | 330 |  |  | 250 | -20.56 |  |

Table 2.0: Line parameters for Base case

| Line parameters |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Line Name (From – To) | Line Number | MW From | Mvar From | MVA From | Lim MVA | % MVA Limit (Max) | MW Loss | Mvar Loss |
| Kebbi - Kanji | 01-02 | -150 | -60 | 161.6 | 773.4 | 20.9 | 2.69 | -97.18 |
| Kanji - Jebba | 02-03 | 208.7 | -31.1 | 211 | 777.3 | 27.1 | 1.26 | -20.99 |
| Jebba - Kanji | 03-02 | -207.4 | 10.1 | 207.6 | 777.3 | 27.1 | 1.26 | -20.99 |
| Shiroro - Jebba | 04-03 | -251.7 | 7.2 | 251.8 | 777.3 | 33.9 | 5.74 | -47.45 |
| Jebba - Shiroro | 03-04 | 257.5 | -54.6 | 263.2 | 777.3 | 33.9 | 5.74 | -47.45 |
| Jebba - Oshogbo | 03-05 | 63.9 | -47.7 | 79.7 | 777.3 | 10.3 | 0.26 | -59.83 |
| Jebba - Oshogbo | 03-05 | 63.9 | -47.7 | 79.7 | 777.3 | 10.3 | 0.26 | -59.83 |
| Jebba Gs - Jebba | 06-03 | 289.2 | 4.2 | 289.2 | 777.3 | 37.2 | 0.24 | -1.1 |
| Jebba Gs - Jebba | 06-03 | 289.2 | 4.2 | 289.2 | 777.3 | 37.2 | 0.24 | -1.1 |
| Shiroro - Katampe | 04-07 | 177.2 | 73.6 | 191.9 | 777.4 | 26.6 | 2.21 | -36.41 |
| Shiroro - Katampe | 04-07 | 177.2 | 73.6 | 191.9 | 777.4 | 26.6 | 2.21 | -36.41 |
| Shiroro - Mando | 04-08 | 249.5 | -73.7 | 260.2 | 777.3 | 33.5 | 2.24 | -19.05 |
| Shiroro -Mando | 04-08 | 249.5 | -73.7 | 260.2 | 777.3 | 33.5 | 2.24 | -19.05 |
| Oshogbo - Benin | 05-17 | -163.4 | -18 | 164.4 | 777.3 | 22.7 | 2.48 | -78.93 |
| Oshogbo - Benin | 05-17 | -163.4 | -18 | 164.4 | 777.3 | 22.7 | 2.48 | -78.93 |
| Oshogbo - Benin | 05-17 | -163.4 | -18 | 164.4 | 777.3 | 22.7 | 2.48 | -78.93 |
| Oshogbo - Ikeja.W | 05-23 | 178.1 | -37.1 | 181.9 | 777.3 | 23.4 | 2.85 | -74.71 |
| Oshogbo - Ayede | 05-33 | 238.5 | -21.4 | 239.4 | 777.3 | 30.8 | 2.32 | -25.54 |
| Mando - Kumbotso | 08-09 | 358.5 | -22.1 | 359.2 | 777.3 | 46.2 | 8.5 | -3.03 |
| Mando - Jos | 08-10 | 77.7 | -94.1 | 122.1 | 777.3 | 15.7 | 0.66 | -76.11 |
| Mando - Jos | 08-10 | 77.7 | -94.1 | 122.1 | 777.3 | 15.7 | 0.66 | -76.11 |
| Mando - Jos | 08-10 | 77.7 | -94.1 | 122.1 | 777.3 | 15.7 | 0.66 | -76.11 |
| Guarara - Mando | 35-08 | 300 | -79.4 | 310.3 | 777.3 | 39.9 | 2.86 | -9.47 |
| Jos - Gombe | 10-11 | 257.1 | -25.6 | 258.4 | 777.3 | 33.2 | 5.84 | -60.4 |

| Jos - Markurdi | 10-36 | -137.9 | -12 | 138.5 | 777.3 | 20.5 | 1.72 | -89.2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Jos - Markurdi | 10-36 | -137.9 | -12 | 138.5 | 777.3 | 20.5 | 1.72 | -89.2 |
| Yola - Gombe | 12-11 | -160 | -90 | 183.6 | 777.3 | 23.6 | 2.89 | -76.65 |
| Damaturu - Gombe | 14-11 | 71.7 | -75.3 | 103.9 | 777.3 | 13.4 | 0.06 | -5.93 |
| Olunrunsogo - Ikeja.W | 13-23 | 55.9 | -0.1 | 55.9 | 777.3 | 9.5 | 0.17 | -48.92 |
| Ayede - Olunrunsogo | 33-13 | 204.8 | -43.8 | 209.5 | 777.3 | 26.9 | 78.95 | -18.28 |
| Damaturu - Maiduguri | 14-15 | 201.8 | -69.9 | 213.6 | 777.3 | 27.5 | 1.83 | -33.27 |
| Damaturu - Mambiya | 14-34 | -403.5 | 75.2 | 410.4 | 777.3 | 53.4 | 7.34 | 14.52 |
| Ikeja.W - Omotosho | 23-16 | 305.5 | 4.4 | 305.5 | 777.3 | 39.3 | 5.48 | 46.54 |
| Ajaokuta - Benin | 18-17 | 156.9 | -53.1 | 165.7 | 777.3 | 21.3 | 1.74 | -62.32 |
| Benin - Ajaokuta | 17-18 | -155.2 | -9.3 | 155.5 | 777.3 | 21.3 | 1.74 | -62.32 |
| Benin - Sapelle | 17-20 | -174.1 | 27.8 | 176.3 | 777.3 | 23.1 | 0.57 | -14.86 |
| Benin - Sapelle | 17-20 | -174.1 | 27.8 | 176.3 | 777.3 | 23.1 | 0.57 | -14.86 |
| Benin - Sapelle | 17-20 | -174.1 | 27.8 | 176.3 | 777.3 | 23.1 | 0.57 | -14.86 |
| Benin - Onitcha | 17-21 | -151.7 | 9.3 | 152 | 777.3 | 20.8 | 1.19 | -43.7 |
| Benin - Onitcha | 17-21 | -151.7 | 9.3 | 152 | 777.3 | 20.8 | 1.19 | -43.7 |
| Benin - Onitcha | 17-21 | -151.7 | 9.3 | 152 | 777.3 | 20.8 | 1.19 | -43.7 |
| Benin - Delta | 17-22 | -241.1 | 25.9 | 242.5 | 777.3 | 31.8 | 2.05 | -20.32 |
| Ikeja.W - Benin | 23-17 | -423.9 | 44.4 | 426.3 | 777.3 | 56.2 | 13.18 | 36.47 |
| Ikeja.W - Benin | 23-17 | -423.9 | 44.4 | 426.3 | 777.3 | 56.2 | 13.18 | 36.47 |
| Geregu - Ajaokuta | 19-18 | 207 | -26.9 | 208.7 | 777.3 | 26.9 | 0.08 | -1.3 |
| Geregu - Ajaokuta | 19-18 | 207 | -26.9 | 208.7 | 777.3 | 26.9 | 0.08 | -1.3 |
| Aladja - Sapelle | 28-20 | 124.4 | -40.9 | 130.9 | 777.3 | 16.8 | 0.37 | -21.5 |
| Onitcha - Alaoji | 21-30 | -597.3 | 115.5 | 608.4 | 777.3 | 79.2 | 18.61 | 104.59 |
| Onitcha - Okpai | 21-31 | -315 | 23.8 | 315.9 | 777.3 | 41.4 | 5 | -11.13 |
| Onitcha - New.H | 21-32 | 338.5 | -22.3 | 339.2 | 777.3 | 43.6 | 3.3 | -3.01 |
| Delta - Aladja | 22-28 | 206.9 | 8.3 | 207 | 777.3 | 26.6 | 0.49 | 4.17 |
| Akangba - Ikeja.W | 24-23 | -235 | -153 | 280.4 | 777.3 | 36.1 | 0.5 | -2.25 |
| Akangba - Ikeja.W | 24-23 | -235 | -153 | 280.4 | 777.3 | 36.1 | 0.5 | -2.25 |
| Papalanto - Ikeja.W | 25-23 | 196 | 17.9 | 196.9 | 777.3 | 25.3 | 1.67 | 14.13 |
| Ikeja.W - Egbin | 23-27 | 67.7 | -84.3 | 108.2 | 777.3 | 13.9 | 0.22 | -22.12 |
| Ayede - Papalanto | 33-25 | -107.7 | -13.1 | 108.5 | 777.3 | 14 | 0.25 | -21.35 |
| Egbin - Aja | 27-26 | 227.9 | 140.6 | 267.8 | 777.3 | 34.6 | 0.36 | -2.36 |
| Egbin - Aja | 27-26 | 227.9 | 140.6 | 267.8 | 777.3 | 34.6 | 0.36 | -2.36 |
| Alaoji - Afam | 30-29 | -304 | 35.2 | 306 | 777.3 | 39.5 | 0.54 | -1.72 |
| Alaoji - Afam | 30-29 | -304 | 35.2 | 306 | 777.3 | 39.5 | 0.54 | -1.72 |
| Afam - Omoku | 29-37 | -82.1 | 3.5 | 82.2 | 777.3 | 10.8 | 0.08 | -12.25 |
| Afam - Ikot E | 29-38 | -38.5 | 8.6 | 39.4 | 777.3 | 7.1 | 0.06 | -30.74 |
| Afam - Ikot E | 29-38 | -38.5 | 8.6 | 39.4 | 777.3 | 7.1 | 0.06 | -30.74 |
| Alaoji - Owerri | 30-40 | -34 | 4.1 | 34.2 | 777.3 | 6.6 | 0.05 | -34.71 |
| Alaoji - Owerri | 30-40 | -34 | 4.1 | 34.2 | 777.3 | 6.6 | 0.05 | -34.71 |

| Markurdi - New.H | 36-32 | -372.1 | 95 | 384 | 777.3 | 50.7 | 13.25 | 13.53 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Markurdi - New.H | 36-32 | -372.1 | 95 | 384 | 777.3 | 50.7 | 13.25 | 13.53 |
| New.H - Ikot E | 32-38 | -548.5 | 87.7 | 555.4 | 777.3 | 72 | 9.18 | 135.87 |
| Markurdi - Mambiya | 36-34 | 142.4 | -50.3 | 151 | 777.3 | 20 | 2.44 | -117.15 |
| Markurdi - Mambiya | 36-34 | 142.4 | -50.3 | 151 | 777.3 | 20 | 2.44 | -117.15 |
| Omoku - Ikot E | 37-38 | -17.2 | 68.6 | 70.8 | 777.3 | 10.1 | 0.04 | -8.21 |
| Ikot E - Calabar | 38-39 | -395.9 | 28.6 | 396.9 | 777.3 | 51.5 | 4.11 | 6.87 |
| Ikot E - Calabar | 38-39 | -395.9 | 28.6 | 396.9 | 777.3 | 51.5 | 4.11 | 6.87 |
| Owerri - Egbema | 40-41 | -248 | 2.7 | 248 | 777.3 | 32.3 | 1.99 | -17.88 |

# 6.0 Three generators contingency (outage)

Gen.

1000.0

500.0

0.0

Gen MW

CASE N-1 contingency analysis: When Egbema, Geregu and Shiroro generators are shut down, the state of generators are well represented in Fig 3. Generators with 0MW are out of service.

Kanji

Shiroro Jebba GS

Olunru… Geregu Sapelle

Delta Papala… Egbin Afam Alaoji Okpai Mambi… Guarara Omoku Calabar Egbema

Fig. 3: Graphical representation of three generators outage.

Effect: Fig. 4, 5 and 6 are diagrams showing system behaviour when three generators are shutdown.

Fig. 4: Voltage contour display when Egbema, Geregu and Shiroro generators were shut down

PU Volt

0.8

0.82

0.84

0.86

0.9

0.88

2

0.94

0.96

0.98

0.91

1.02

1.04

Voltage Display

Line Losses

200

150

100

50

0

% MVA Limit

Kebbi

Jebba Oshogbo Katampe Kumbotso Gombe Olunrunsogo Maiduguri

Benin Geregu Onitcha Ikeja.W Papalanto

Egbin Afam Okpai Ayede Guarara Omoku Calabar

Egbema

Fig. 5: Voltage graphical display when Egbema, Geregu and Shiroro generators were shut down

Kebbi -…

Jebba -… Jebba Gs… Shiroro -… Oshogbo… Mando -…

Jos -… Olunruns… Ikeja.W -… Benin -…

Benin -… Geregu -… Onitcha -… Akangba… Egbin - Aja

Afam -… Alaoji -… Markurd… Ikot E -…

Fig.6: Line graphical display when Egbema, Geregu and Shiroro generators were shut down

Observation: When three generators were shutdown, Bus 4,7,8,9 and 12 voltage was violated with per unit value 0.8865, 0.82149, 0.92961, 0.86505 and 0.90487 respectively. This means that the affected bus voltage value have crossed the required voltage limit. Fig. 5 was plotted using during outage parameter in table 3.0.

Moreover, all line parameters are within its safe limit excluding line Ikeja west to Egbin with violated percentage MVA value of 162, this can be seen in table 4.0. Fig. 6 was plotted using during outage parameter in table 4.0.

# 6.1 Remedial Actions

Generator outage led to voltage and line MVA limit violation. Reactive power compensation which involve addition of shunt capacitor value 200MVar and 400MVar in bus 6 (Jebba) and bus 4 (Shiroro) respectively was done to clear voltage violation. Thus, double line circuit action between Ikeja West and Egbin ensured line violation clearance. Post correction data of table 3.0 and table 4.0 produced fig. 8 and 9 respectively. Fig. 7, 8 and 9 are diagrams showing system behaviour after these actions were taken.

Kebbi Jebba Oshogbo Katampe Kumbotso Gombe Olunrunsogo Maiduguri

Benin Geregu Onitcha Ikeja.W Papalanto

Egbin Afam Okpai Ayede Guarara Omoku Calabar Egbema

Kebbi - Kanji Jebba - Shiroro

Jebba Gs -… Shiroro -… Oshogbo -…

Mando - Jos Jos - Markurdi Olunrunsogo…

Ikeja.W -…

Benin - Sapelle

Benin -… Geregu -… Onitcha -… Akangba -… Ayede -…

Alaoji - Afam Alaoji - Owerri New.H - Ikot E Ikot E - Calabar

112

Ani et. al. / Journal of Engineering and Applied Sciences 12 (2018), 103-116

Fig. 7: Voltage contour display after corrective actions were taken

Voltage Display

1.05

1.03

1.01

0.99

0.97

0.95

PU Volt

Fig. 8: Voltage graphical display after corrective actions were taken

Line Losses

100

80

60

40

20

0

% MVA Limit

Fig. 9: Line graphical representation after corrective actions were taken

JEAS ISSN: 1119-8109

# Bus record

Table 3.0: Voltage parameters data during generators outage and after remedial (post correction) action was taken

| BUS |  | DURING OUTAGE |  |  | POST CORRECTION |  |
| --- | --- | --- | --- | --- | --- | --- |
| Number | Name | PU Volt | Volt (kV) | Nom kV | PU Volt | Volt (kV) |
| 1 | kebbi | 0.97127 | 320.518 | 330 | 0.97127 | 320.518 |
| 2 | kanji | 1 | 330 | 330 | 1 | 330 |
| 3 | jebba | 0.99419 | 328.083 | 330 | 0.99852 | 329.513 |
| 4 | shiroro | 0.8865 | 292.543 | 330 | 1.01732 | 335.714 |
| 5 | oshogbo | 1.00475 | 331.568 | 330 | 1.01652 | 335.452 |
| 6 | jebba GS | 1 | 330 | 330 | 1 | 330 |
| 7 | katampe | 0.82149 | 271.092 | 330 | 0.96654 | 318.957 |
| 8 | mando | 0.92961 | 306.77 | 330 | 1.02685 | 338.86 |
| 9 | kumbotso | 0.86505 | 285.466 | 330 | 1.0237 | 337.821 |
| 10 | jos | 0.96438 | 318.247 | 330 | 1.04388 | 344.48 |
| 11 | gombe | 0.97211 | 320.795 | 330 | 1.0138 | 334.554 |
| 12 | yola | 0.90487 | 298.606 | 330 | 0.9549 | 315.117 |
| 13 | olunrunsogo | 1 | 330 | 330 | 1 | 330 |
| 14 | damaturu | 0.97227 | 320.85 | 330 | 1.01023 | 333.375 |
| 15 | maiduguri | 0.97711 | 322.446 | 330 | 1.02152 | 337.103 |
| 16 | omotosho | 0.97798 | 322.733 | 330 | 0.99262 | 327.566 |
| 17 | benin | 1.00582 | 331.921 | 330 | 1.01185 | 333.911 |
| 18 | ajaokuta | 1.00991 | 333.271 | 330 | 1.01622 | 335.353 |
| 19 | geregu | 1.00993 | 333.276 | 330 | 1.01624 | 335.358 |
| 20 | sapelle | 1 | 330 | 330 | 1 | 330 |
| 21 | onitcha | 0.99157 | 327.217 | 330 | 1.00067 | 330.222 |
| 22 | delta | 1 | 330 | 330 | 1 | 330 |
| 23 | ikeja.w | 0.98662 | 325.583 | 330 | 0.9975 | 329.176 |
| 24 | akangba | 0.97716 | 322.461 | 330 | 0.98815 | 326.09 |
| 25 | papalanto | 1 | 330 | 330 | 1 | 330 |
| 26 | Aja | 0.99279 | 327.622 | 330 | 0.99279 | 327.622 |
| 27 | egbin | 1 | 330 | 330 | 1 | 330 |
| 28 | aladja | 0.99702 | 329.016 | 330 | 0.99702 | 329.016 |
| 29 | afam | 1 | 330 | 330 | 1 | 330 |
| 30 | alaoji | 1 | 330 | 330 | 1 | 330 |
| 31 | okpai | 1 | 330 | 330 | 1 | 330 |
| 32 | new.h | 0.95797 | 316.132 | 330 | 0.98174 | 323.974 |
| 33 | ayede | 0.9978 | 329.275 | 330 | 1.00027 | 330.09 |
| 34 | mambiya | 1 | 330 | 330 | 1 | 330 |
| 35 | guarara | 1 | 330 | 330 | 1 | 330 |
| 36 | markurdi | 0.96796 | 319.428 | 330 | 1.01339 | 334.42 |
| 37 | omoku | 1 | 330 | 330 | 1 | 330 |

| 38 | ikot e | 0.99421 | 328.088 | 330 | 0.99537 | 328.473 |
| --- | --- | --- | --- | --- | --- | --- |
| 39 | calabar | 1 | 330 | 330 | 1 | 330 |
| 40 | owerri | 0.99608 | 328.707 | 330 | 0.99608 | 328.707 |
| 41 | egbema | 1.0008 | 330.265 | 330 | 1.0008 | 330.265 |

# Line Record

Table 4.0: Line parameters data during generators outage and after remedial (post correction) action was taken

| LINE DATA | DURING OUTAGE |  |  |  | POST-CORRECTION DATA |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| From - To | % of MVA Limit (Max) | MW Loss | Mvar Loss | Lim MVA | % of MVA Limit (Max) | MW Loss | Mvar Loss |
| Kebbi - Kanji | 20.9 | 2.69 | -97.18 | 773.4 | 20.9 | 2.69 | -97.18 |
| Kanji - Jebba | 26.9 | 1.26 | -20.89 | 777.3 | 27.1 | 1.26 | -20.99 |
| Jebba - Kanji | 26.9 | 1.26 | -20.89 | 777.3 | 27.1 | 1.26 | -20.99 |
| Shiroro - Jebba | 66.8 | 24.7 | 126.35 | 777.3 | 64.6 | 21.53 | 86.61 |
| Jebba - Shiroro | 66.8 | 24.7 | 126.35 | 777.3 | 64.6 | 21.53 | 86.61 |
| Jebba - Oshogbo | 23.5 | 1.83 | -46.19 | 777.3 | 23.6 | 1.82 | -47.28 |
| Jebba - Oshogbo | 23.5 | 1.83 | -46.19 | 777.3 | 23.6 | 1.82 | -47.28 |
| Jebba Gs - Jebba | 45.5 | 0.36 | -0.06 | 777.3 | 37.4 | 0.24 | -1.08 |
| Jebba Gs - Jebba | 45.5 | 0.36 | -0.06 | 777.3 | 37.4 | 0.24 | -1.08 |
| Shiroro - Katampe | 26.6 | 3.03 | -16.73 | 777.4 | 26.6 | 2.12 | -39.29 |
| Shiroro - Katampe | 26.6 | 3.03 | -16.73 | 777.4 | 26.6 | 2.12 | -39.29 |
| Shiroro - Mando | 30.3 | 2.22 | -12.21 | 777.3 | 24.5 | 1.12 | -29.84 |
| Shiroro -Mando | 30.3 | 2.22 | -12.21 | 777.3 | 24.5 | 1.12 | -29.84 |
| Oshogbo - Benin | 19.1 | 1.69 | -86.17 | 777.3 | 19.8 | 1.75 | -87.43 |
| Oshogbo - Benin | 19.1 | 1.69 | -86.17 | 777.3 | 19.8 | 1.75 | -87.43 |
| Oshogbo - Benin | 19.1 | 1.69 | -86.17 | 777.3 | 19.8 | 1.75 | -87.43 |
| Oshogbo - Ikeja.W | 14.7 | 0.77 | -92.56 | 777.3 | 14.7 | 0.72 | -95.24 |
| Oshogbo - Ayede | 11.8 | 0.28 | -42.93 | 777.3 | 13.5 | 0.34 | -43.1 |
| Mando - Kumbotso | 47.4 | 11.02 | 33.71 | 777.3 | 46.4 | 8.2 | -8.83 |
| Mando - Jos | 12.1 | 0.35 | -66.9 | 777.3 | 10.2 | 0.17 | -82.02 |
| Mando - Jos | 12.1 | 0.35 | -66.9 | 777.3 | 10.2 | 0.17 | -82.02 |
| Mando - Jos | 12.1 | 0.35 | -66.9 | 777.3 | 10.2 | 0.17 | -82.02 |
| Guarara - Mando | 48.7 | 4.6 | 7.95 | 777.3 | 42.8 | 3.23 | -6.89 |
| Jos - Gombe | 29.2 | 4.84 | -57.2 | 777.3 | 30.2 | 4.79 | -70.41 |
| Jos - Markurdi | 26.6 | 3.76 | -58.81 | 777.3 | 28.8 | 3.64 | -72.07 |
| Jos - Markurdi | 26.6 | 3.76 | -58.81 | 777.3 | 28.8 | 3.64 | -72.07 |
| Yola - Gombe | 23.6 | 3.22 | -65.28 | 777.3 | 23.6 | 2.86 | -77.62 |
| Damaturu - Gombe | 14.2 | 0.07 | -5.34 | 777.3 | 16.6 | 0.09 | -5.69 |
| Olunrunsogo - Ikeja.W | 15.2 | 0.53 | -45.82 | 777.3 | 13.3 | 0.43 | -47.25 |
| Ayede - Olunrunsogo | 7.4 | 78.39 | -23.44 | 777.3 | 7.1 | 78.58 | -23.53 |

| Damaturu - Maiduguri | 26.8 | 1.9 | -29.02 | 777.3 | 27.5 | 1.82 | -33.61 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Damaturu - Mambiya | 58.1 | 8.91 | 29.52 | 777.3 | 56.6 | 8.23 | 21.95 |
| Ikeja.W - Omotosho | 39.3 | 5.5 | 46.64 | 777.3 | 39.3 | 5.37 | 45.58 |
| Ajaokuta - Benin | 9.2 | 0.21 | -76.42 | 777.3 | 9.3 | 0.21 | -77.39 |
| Benin - Ajaokuta | 9.2 | 0.21 | -76.42 | 777.3 | 9.3 | 0.21 | -77.39 |
| Benin - Sapelle | 24 | 0.6 | -14.61 | 777.3 | 26.2 | 0.71 | -13.82 |
| Benin - Sapelle | 24 | 0.6 | -14.61 | 777.3 | 26.2 | 0.71 | -13.82 |
| Benin - Sapelle | 24 | 0.6 | -14.61 | 777.3 | 26.2 | 0.71 | -13.82 |
| Benin - Onitcha | 8.1 | 0.08 | -53.1 | 777.3 | 7.6 | 0.07 | -53.99 |
| Benin - Onitcha | 8.1 | 0.08 | -53.1 | 777.3 | 7.6 | 0.07 | -53.99 |
| Benin - Onitcha | 8.1 | 0.08 | -53.1 | 777.3 | 7.6 | 0.07 | -53.99 |
| Benin - Delta | 32.2 | 2.09 | -20.18 | 777.3 | 33 | 2.16 | -19.75 |
| Ikeja.W - Benin | 11.4 | 0.36 | -73.33 | 777.3 | 11.5 | 0.41 | -74.27 |
| Ikeja.W - Benin | 11.4 | 0.36 | -73.33 | 777.3 | 11.5 | 0.41 | -74.27 |
| Geregu - Ajaokuta | 0.3 | 0 | -2 | 777.3 | 0.3 | 0 | -2.02 |
| Geregu - Ajaokuta | 0.3 | 0 | -2 | 777.3 | 0.3 | 0 | -2.02 |
| Aladja - Sapelle | 16.8 | 0.37 | -21.51 | 777.3 | 16.8 | 0.36 | -21.54 |
| Onitcha - Alaoji | 53.3 | 8.41 | 17.89 | 777.3 | 53.7 | 8.46 | 17.84 |
| Onitcha - Okpai | 41.3 | 5 | -10.88 | 777.3 | 41.6 | 5.01 | -11.24 |
| Onitcha - New.H | 74.5 | 9.85 | 53.81 | 777.3 | 70.7 | 8.67 | 42.76 |
| Delta - Aladja | 26.6 | 0.49 | 4.16 | 777.3 | 26.5 | 0.49 | 4.14 |
| Akangba - Ikeja.W | 36.1 | 0.5 | -2.23 | 777.3 | 36.1 | 0.49 | -2.46 |
| Akangba - Ikeja.W | 36.1 | 0.5 | -2.23 | 777.3 | 36.1 | 0.49 | -2.46 |
| Papalanto - Ikeja.W | 6.1 | 0.1 | 0.83 | 777.3 | 4.8 | 0.06 | 0.52 |
| Ikeja.W - Egbin | 161.8 | 35.17 | 274.32 | 777.3 | 78.3(2) | 8.2 (2) | 45.29(2) |
| Ayede - Papalanto | 34.8 | 1.56 | -10.24 | 777.3 | 34.6 | 1.54 | -10.48 |
| Egbin - Aja | 34.6 | 0.36 | -2.36 | 777.3 | 34.6 | 0.36 | -2.36 |
| Egbin - Aja | 34.6 | 0.36 | -2.36 | 777.3 | 34.6 | 0.36 | -2.36 |
| Alaoji - Afam | 42.5 | 0.63 | -0.99 | 777.3 | 42.6 | 0.63 | -0.97 |
| Alaoji - Afam | 42.5 | 0.63 | -0.99 | 777.3 | 42.6 | 0.63 | -0.97 |
| Afam - Omoku | 13.3 | 0.12 | -11.88 | 777.3 | 13.4 | 0.13 | -11.88 |
| Afam - Ikot E | 8.9 | 0.1 | -30.33 | 777.3 | 8.5 | 0.1 | -30.42 |
| Afam - Ikot E | 8.9 | 0.1 | -30.33 | 777.3 | 8.5 | 0.1 | -30.42 |
| Alaoji - Owerri | 11.9 | 0.26 | -32.95 | 777.3 | 11.9 | 0.26 | -32.95 |
| Alaoji - Owerri | 11.9 | 0.26 | -32.95 | 777.3 | 11.9 | 0.26 | -32.95 |
| Markurdi - New.H | 61.2 | 21.5 | 93.35 | 777.3 | 60.2 | 19.48 | 69.34 |
| Markurdi - New.H | 61.2 | 21.5 | 93.35 | 777.3 | 60.2 | 19.48 | 69.34 |
| New.H - Ikot E | 66.7 | 7.98 | 111.36 | 777.3 | 65.9 | 7.71 | 103.48 |
| Markurdi - Mambiya | 24.5 | 3.6 | -99.29 | 777.3 | 21.4 | 2.87 | -111.73 |
| Markurdi - Mambiya | 24.5 | 3.6 | -99.29 | 777.3 | 21.4 | 2.87 | -111.73 |
| Omoku - Ikot E | 13.1 | 0.08 | -7.93 | 777.3 | 11.1 | 0.05 | -8.13 |

| Ikot E - Calabar | 51.5 | 4.11 | 6.89 | 777.3 | 51.5 | 4.11 | 6.87 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Ikot E - Calabar | 51.5 | 4.11 | 6.89 | 777.3 | 51.5 | 4.11 | 6.87 |
| Owerri - Egbema | 4.5 | 0.01 | -34.74 | 777.3 | 4.5 | 0.01 | -34.74 |

# Results and Discussions

The bus labelled Egbim, which is the system slack bus generates active power of 657 MW and reactive power of

450.85 MVar. As such this indicates that the loads on the system require more power than is supplied by the generators and this deficit is taken care of by the slack bus. In the event that there is excess power in the system, the slack bus will in turn draw this power.

From bus contour diagrams, the coloured background shows the voltage difference among the system. The red means the highest voltage and blue means the lowest voltage. The simulation diagram is shown in Fig. 2.

Line power flow is said to be violated when the actual power flow post contingency exceeds the line flow limits which depend on the protection relay settings. Some contingencies lead to line flow violations, and some of them do not lead to any violations. The lines connecting the different buses have set thermal ratings. As the power requirements are adjusted, the flow of active and reactive power from and to the generators through the lines also changes. These changes are monitored by the pie charts that are indicated on each of the transmission lines in the system. The charts provide an elaborate warning scheme to guard against exceeding the line parameters.

# Conclusion

This article analysed the probable contingencies on the Nigeria 330kv post reform integrated power system in order to explore uncertainties, effects of alternative internal and external changes in the power systems and to identify limitations that can affect the power reliability and security operations. It examined method for power system contingency study with techniques from available pattern that is recognised. The methods use the measured variables, such as bus admittance, busbar voltage, active and reactive power of generator, etc. to decide the state of the power system. This could make it easier to decide what needs to be done by the system operators to avoid blackout.

# References

Billinton, R. and Allan, R.N. (1994). Reliability Evaluation of Power Systems. Plenum press, 2nd edition.

Chary, D. M. (2011). Contingency Analysis in Power Systems, Transfer Capability Computation and Enhancement Using Facts Devices in Deregulated Power System. Ph.D. diss., Jawaharlal Nehru Technological University.

ENTSOE (European Network of Transmission System Operators for Electricity). Nordic Grid Code 2007 (Nordic collection of rules). Available online: https://www.entsoe.eu/index.php?id=62.G. Wacker and R. Billinton. Customer cost of electric service interruptions. Proceedings of the IEEE, 77(6):919–930, June 1989.

Gupta, J.B. (2008). A course in power systems. S.K. Kataria and Sons, Darya Ganji, New Delhi- 1100002.

Nigeria Compass (2013); Nigeria's Power Generation hits 5,228 Mega Watt.

Available:http://www.compassnewspaper.org/index.php/special-desk/businessnews/12769-nigerias-power- generation-hits-5228-megawatts.